|  | Hazardous Area – Electrical Equipment Inspection Test Report | ITR 22 |
| --- | --- | --- |

| Asset: |  | Contractor: |  | Ref No: |  |
| --- | --- | --- | --- | --- | --- |
| Equipment / Tag No: |  | Equipment Title: |  |
| Manufacturer: |  | Model: |  |
| Equip Serial No: |  | Ex Certification No: |  |
| Area Classification: | Zone |  | Gas Group: |  | Temp Class: |  | Amb: oC |
| Equipment Classification: | Ex Technique |  | Gas Group: |  | Temp Class: |  | Amb: oC |
| Reference Drawings: |  |
| Notes: | 1) | All fields are to be completed. Any non-applicable fields shall state “NA”. Comments are required for ‘NA’ and ‘Reject’ columns. |
| ITEM | EQUIPMENT | DETAILED INSPECTION RESULTS |
|  |  | OK | NA | Reject | COMMENTS |
| 1 | Equipment is clearly marked with Ex identification (Compliance Plate) |  |  |  |  |
| 2 | Equipment Gas Group is correct for the Area |  |  |  |  |
| 3 | Equipment Temperature Class is correct for the Area |  |  |  |  |
| 4 | Equipment has IP rating appropriate to location |  |  |  |  |
| 5 | Installation in accordance with documentation (incl. conditions on cert. - X) |  |  |  |  |
| 6 | Equipment Ex Technique Appropriate for Area Classification (Items 1/2/3/4/5) |  |  |  |  |
| 7 | Equipment circuit identification is available & correct C F T |  |  |  |  |
| 8 | Sealing gaskets or compounds on glasses / windows are satisfactory |  |  |  |  |
| 9 | Enclosure gaskets condition is satisfactory (clean, undamaged) |  |  |  |  |
| 10 | Equipment NOT obviously damaged |  |  |  |  |
| 11 | There are NO visible unauthorized modifications |  |  |  |  |
| 12 | Fixtures (bolts, covers) appear to be correct type, complete and tight |  |  |  |  |
| 13 | Unused entry plugs are correct type for Ex technique, complete and tight |  |  |  |  |
| 14 | Lamp rating, type and position are correct |  |  |  |  |
| 15 | Cable glands have correct Ex rating identified (d or de) and installed correctly |  |  |  |  |
| 16 | Cables / conduits not obviously damaged |  |  |  |  |
| 17 | Cable type is appropriate and Installed in accordance with Documentation |  |  |  |  |
| 18 | All unused cores are terminated |  |  |  |  |
| 19 | Electrical connections are correct (Clearances, creepage, terminations tight) |  |  |  |  |
| 20 | All unused cores are earthed at one end |  |  |  |  |
| 21 | Earthing Continuity & Equipotential Bonding appear to be satisfactory |  |  |  |  |
| 21 | Earth loop impedance / resistance is satisfactory (sight test documents) |  |  |  |  |
| 22 | Insulation resistance is satisfactory (sight test documents) |  |  |  | Value (ohm)= |
| 23 | Equip protected against corrosion / weather / vibration / other adverse conditions |  |  |  |  |
| 24 | No undue accumulation of dust and moisture |  |  |  |  |
| 25 | Electrical insulation is clean and dry |  |  |  |  |
| 26 | All moving parts are free and has no obvious mechanical damage |  |  |  |  |
| 27 | Electrical Protection Devices set correctly and operate within permitted limits |  |  |  |  |
| Extra Ex d checks |
| 28 | Ex d conduits seals are fitted to all conduits |  |  |  |  |
| 29 | Conduits seals are satisfactorily sealed |  |  |  |  |
| 30 | Adaptors, nipples, tees, etc. are all certified Ex d |  |  |  |  |
| 31 | No obstacles within 40mm of flange joints |  |  |  |  |
| 32 | Flame paths are clean and undamaged |  |  |  |  |
| 33 | Flange gap dimensions are within tolerances |  |  |  |  |

| ITEM | EQUIPMENT | DETAILED INSPECTION RESULTS |
| --- | --- | --- |
|  |  | OK | NA | Reject | COMMENTS |
| Extra Ex e checks |
| 34 | All Equipment is Ex e certified (including components within Enclosure) |  |  |  |  |
| 35 | The No. of Components within Enclosure does not exceed permitted maxima |  |  |  |  |
| 36 | Bridging links do not reduce creepage / clearance and are allowed |  |  |  |  |
| 37 | Power conductors are not bunched together causing possible hot spots |  |  |  |  |
| 38 | Unused Terminals are tightened down |  |  |  |  |
| 39 | All Terminals are Ex n certified (if required on certificate) |  |  |  |  |
| 40 | Bridging links do not reduce creepage / clearance and are allowed |  |  |  |  |
| 41 | Hermetically sealed and Enclosed Break devices are undamaged |  |  |  |  |
| Extra Ex nR (Restricted Breathing) checks |
| 42 | Gaskets and seals are in good condition |  |  |  |  |
| 43 | Pressure test points are available for testing |  |  |  |  |
| Extra Ex p checks |
| 44 | Pressurisation Gas is correct type |  |  |  |  |
| 45 | Actual pressure is within maximum and minimum settings for Equipment |  |  |  |  |
| 46 | Timers set as per certification documentation |  |  |  |  |
| 47 | Alarms and Trip functions operate correctly as per certification Documentation |  |  |  |  |
| Extra Ex i (Intrinsically Safe – IS) checks |
| 48 | Equipment has adequate Circuit Identification for ‘IS’ Installation |  |  |  |  |
| 49 | Point-to-Point checks are OK (sight test Documentation). |  |  |  |  |
| 50 | All cable cores are uniquely labeled (Check loop termination schedules) |  |  |  |  |
| 51 | Cable screens are isolated at one end (usually field side) |  |  |  |  |
| 52 | All Cable Screens and associated equipment are earthed as per requirement |  |  |  |  |
| 53 | Cable length for entire Loop is stated (and less than max allowable Length) |  |  |  | Length (m) = |
| 54 | Separation and segregation is maintained between IS and non-IS Circuits |  |  |  |  |
| 55 | Earth Free test for IS installation (to prove IS earth) – check Test sheet |  |  |  |  |
| 56 | IS Barrier, energy limiting devices, fuses, Power Supply are Cert. approved |  |  |  |  |
| 57 | BARRIER: | Model No: |  | Make: |  | Serial No: |  | Ex Cert No: |  |
| REMARKS: |  |
| PUNCH LIST CATEGORY |
| A |  | B |  | C |  |
| REVIEWED & ACCEPTED: |
|  | Inspector | Supervisor | Client Responsible Engineer |
| NAME (print): |  |  |  |
| SIGNATURE: |  |  |  |
| DATE: |  |  |  |